File Name:		SSM4370_2.6.0.NEI/XIF/NXE

Firmware ID:	SSM4370

Device: 		FX06/07/14 Lon Com Card

EC:			LO1525-07

Release date:	November 5, 2007

Release reason:	Bug fixing

Bug fixing contents:

| Clearquest | Title | Details |
| --- | --- | --- |
| NEWPR00001960 (Probtrak 137621) | LON communication problems | NVI’s are not recovered by the device after autorestore of the NAE |
| NEWPR00002661 (Probtrak 138130) | LON communication problems | NVI/NVO sets to Off at initialization and then invalid. Time at off was too long for NAE system |
| NEWPR00002268 (Probtrak 137945/138134) | LON communication problems | Writing action corrupted the Lon card memory after reset. Memory buffer was wrongly initialized (FX15/FX16 only) |

File Name:		FX0614_V25_00.NEI/XIF/NXE

Firmware ID:	SSM_4370

Device: 		FX06/07/14 Lon Com Card

Release date:	December  6, 2006

Release reason:	Compatibility with Builder 4.X apd format

Note:   	.XIF and .NXE files are downloaded by commissioning tool in the LCC

.NEI file is the file used to program the flash

New FX06/07/14 Lon Card FW is released in order to be compatible with following apd format:

- Builder 3.X

- Builder 4.x