File Name:		SSM4400_2.6.0.NEI/XIF/NXE

Firmware ID:	SSM4400

Device: 		FX15/16/16+ Lon Com Card

EC:			LO1525-07

Release date:	November 5, 2007

Release reason:	Bug fixing

Bug fixing contents:

| Clearquest | Title | Details |
| --- | --- | --- |
| NEWPR00001960 (Probtrak 137621) | LON communication problems | NVI’s are not recovered by the device after autorestore of the NAE |
| NEWPR00002661 (Probtrak 138130) | LON communication problems | NVI/NVO sets to Off at initialization and then invalid. Time at off was too long for NAE system |
| NEWPR00002268 (Probtrak 137945/138134) | LON communication problems | Writing action corrupted the Lon card memory after reset. Memory buffer was wrongly initialized (FX15/FX16 only) |

File Name:		FX1516_V25_00.NEI/XIF/NXE

Firmware ID:	SSM_4400

Device: 		FX15/16 Lon Com Card

Release date:	Jan 30, 2007

Release reason:	Bug fixing

Note:   .XIF and .NXE files are downloaded by commissioning tool in the LCC

.NEI file is the file used to program the flash

CQ1829# Initialization of NVO connected to DI is not done correctly on FX15 Univ + Lon

File Name:		FX1516_V24_00.NEI/XIF/NXE

Firmware ID:	SSM_4400

Device: 		FX15/16 Lon Com Card

Release date:	Dec 6, 2006

Release reason:	Compatibility with Builder 4.X apd format

Note:   	.XIF and .NXE files are downloaded by commissioning tool in the LCC

.NEI file is the file used to program the flash

New FX15/16 Lon Card FW is released in order to be compatible with following apd format:

- Builder 3.X

- Builder 4.x