File Name:		SSM4364_3.23.0_B.a37

Firmware ID:	Fx06 - v3.23.00.a37

Device: 		FX06 controller

Release date:	March 16, 2009

Release reason:	Fixing

Issue document:	LO1661-09

Following defects have been fixed:

| PT140227 | MASTER SLAVE COMMUNICATION | Time scheduler output status sent from master to slave is sometimes lost on the slave |
| --- | --- | --- |

File Name:		SSM4364_3.22.0_B.a37

Firmware ID:	Fx06 - v3.22.00.a37

Device: 		FX06 controller

Release date:	February 18, 2009

Release reason:	Fixing

Issue document:	LO1656-09

Following defects have been fixed:

| 3182 | Integrated LCD display not operating | Integrated display goes sometimes blank. The controller is still operating but user cannot interact becuase the display is not usable. |
| --- | --- | --- |

File Name:		SSM4364_3.21.0_B.a37

Firmware ID:	Fx06 - v3.21.00.a37

Device: 		FX06 controller

Release date:	September 15, 2008

Release reason:	Fixing

Issue document:	LO1627-08

Following issues have been fixed

| PROBTRAK | CQ | DESCRIPTION |
| --- | --- | --- |
| 138206 | 2976 | Display unit of measure with remote display |
| 140051 | 2975 | NRM communication. Some FX messages have an incomplete checksum. It makes unreliable some values on NRM display (i.e.: situation occurs with application where temperatureoffset parameter was set from tool at a value different from 0) |

Feedback from field shows that FX07 (230V model) was affected by strong electromagnetic disturbances (higher than the CE homologations). As a Consequence AD converter of the analogue inputs blocked and sensor measurements were frozen. In order to improve device robustness, AD converter firmware management has been modified (periodic reset in order to prevent any AI freeze situation)

File Name:		SSM4364_3.20.3_B.a37

Firmware ID:	Fx06 - v3.20.03.a37

Device: 		FX06 controller

Release date:	June 6, 2008

Release reason:	Fixing

Issue document:	LO1607-08

Following issues have been fixed

| PROBTRAK | CQ | DESCRIPTION |
| --- | --- | --- |
| 139329 | 2785 | MODEM: ODD phone number not supported |
| 138727 | 2860 | N2 COMMUNICATION: Override and release N2 command not well supported |
|  | 2654 | OBJECT: Clock and date set object revision, Daylight saving bug when clock was modified within the week before the clock change |
|  | 2814 | OBJECT: PAT object revision, Priority change between normal operations and resynch cycle |
|  | 2856 | OBJECT: shared object list (semi-hermetic compressor, EWMA) |
|  | 2861 | OBJECT: New on-off output object revision, Antisticking and short cycle functions not working |
|  | 2931 | OBJECT: AO behavior at disable, At disable active, output was set to 0%. On the contrary DO output was frozen. AO behavior has been aligned with DO one. AO is now frozen when disable |
| 139865 | 2938 | NRM: unplug issue, NRM was not recovered after communication bus unplugged |

File Name:		SSM4364_3.17.0_B.a37

Firmware ID:	Fx06 - v3.17.a37

Device: 		FX06 controller

Release date:	November 7, 2007

Release reason:	Fixing

Issue document:	LO1563-07

Following issues have been fixed

| CQ Number | Description |
| --- | --- |
| NEWPR00001449 | INTEGRATED DISPLAY: Alarm acknowledgment implementation |
| NEWPR00001460 | INTEGRATED DISPLAY: Sub menu of the On-off scheduler was not always shown |
| NEWPR00001551 | INTEGRATED DISPLAY: “too many exceptions” system string didn’t scroll (only “too” was visible) |
| NEWPR00001974 | MEMORY: allocated backup memory was 62 bytes instead of 64 |
| NEWPR00002296 (PT 137968) | INTEGRATED DISPLAY: when event history was displayed, icons disappear and come back only if even status changes |
| NEWPR00002348 | PWM output: PWM went randomly to 0 |
| NEWPR00002388 | INTEGRATED DISPLAY: event pop up new management, when all current events are no more active, the pop up message disappears too |
| NEWPR00002514 | OBJECT: USD time zones were not properly defined on new clock and date set object |
| NEWPR00002620 | TREND: at circular buffer full, trends are not working properly after device power cycle |
| NEWPR00002646 | Output override feature |
| NEWPR00002666 (PT138976) | The FX06 controller, will sometimes display BYE on the user interface. This may occur after an abrupt power interruption |

File Name:		SSM4364_03200_B.a37

Firmware ID:	Fx06 - v3.02.a37

Device: 		FX06 controller

Release date:	March 09, 2007

Release reason:	Fixing

Issue document:	LO1515-07

The firmware new version  fixes the following defects present on the firmware 3.01

| Clearquest | Title | Details |
| --- | --- | --- |
| NEWPR00001896 (Probtrak 137560) | N2 communication problems: AI/BI regions | Bad answer of the device to a READ or COS command through N2 communication bus 1) Point defines as AI type frequently becomes OffLine 2) COS response is abnormal with point defined as BI type |
| NEWPR00001917 (Probtrak 137620) | N2 communication problems: wrong values sent by device at power on | Field feedback: NVOs(BI) defined as SNVT_switch outputs go ON momentarily when the power supply of FX07 is turned off and on. Solution: device is waiting to be completely initialized before to accept write or read command |

File Name:		SSM4364_03101.a37

Firmware ID:	Fx06 - v3.01.a37

Device: 		FX06 controller

Release date:	Jan 09, 2007

Release reason:	Fixing

Issue document:	LO1501-07

The following defects have been fixed regarding to the version 3.00

NEWPR00001863:	Calibration Error.

“Calibrations of the Ratio metric sensor are not retained”.

Reminder:

* the firmware fixes the following defects present on the firmware 1.03

| Clearquest | Title | Details |
| --- | --- | --- |
| NEWPRO00001254 NEWPRO00001783 (Probtrak 137086) | Backup Memory | All the output object normally saved in the backup memory are not memorized at power down (Counters, integrator, general setpoint, …) |
| NEWPRO00000781 | General Setpoint | HMI object output not managed correctly by the display |
| NEWPRO00001488 (Probtrak 136705) | Modem management | When FX06 and modem are switched at the same, after FX06 initialization, the modem is not correctly configured. As a consequence SMS are not sent |

* Firmware introduces also the following features

New objects in the library:

Extended objects

- Analogue input

- Digital input

- Occupancy Input

- Analogue output

- PAT, DAT, Damper PAT

- On-Off output

Calculation objects

- Maximum

- Average

- Selector

- span

Logic objects

- NO, AND, OR, XOR

Other objects

- System resource

- Fan controller

- N2 room module sensor

New features:

Application Management

- Trend management

- Upgraded object library (see below Analogue input

Local display

- Time scheduler management

- Event History management Average

Remote display management

- Event History management

- Trend management

Events

- Storage (Event History)

Supervisor link

- Trended data file upload

Known defects:

NEWPR00000107:	FX06: Alarm visualization on MUI is not correct.

Define on Event Maker an alarm with EventName greater than 20 characters.

The Alarm visualization in Event Summary on MUI is not correct.

NEWPR00000430:	LON: Stress Test: Network communication error

1) By LonMaker tool commission the FX14 in the attached network (LonMaker Backup file);

2) Try to modify some nvi in the Browser Lon;

Result: sometime a "Network error" message appears in the warning message;

3) Enable the polling in the Browser Lon

Result: A "Communication failure while monitoring the object" message appears very frequently in the warning message;

NEWPR00000428:	LON: Alias Connections behavior

If connect an nvo of the FX14/06  to a two nvi of the another device, only the primary connection works good and the value is correctly trasmitted. The Alias connection doesn't work.

NEWPR00001480:	LCD2x4 : the sub-menu for the "OnOff Scheduler" is not always shown.

The "OnOff Schedulers" sub-menu is NOT shown, on the Local Display of the Device, if the order of the Scheduler points in the Display "LCD2x4" is the following :

1) Calendar (40070);

2) OnOff Scheduler (40060);

3) OnOff Scheduler Alternate (40061).

The sub-menu is correctly shown in case of different order

NEWPR00001548:	Sms Management : The Event via SMS is not sent after a GSM Modem power-off/power-on:

Operations to repeat the problem :

- FX06 connected to a GSM Modem

- Power-On the Configuartion (Modem and Device);

- Enable an event with associated SMS notification, the SMS is correctly sent;

- Power-Off GSM Modem;

- Power-On GSM Modem;

- Enable an event with associated SMS notification, the SMS is not sent;

To restore the correct behavior the user has to Power-Off and Power-On the device;

Note : the same problem has been verified disconnecting the cable from Modem to Device.

NEWPR00001551:     The "Too Many Exception" system text doesn't scroll.

This system text appears when more than 25 events are defined for the Calendar Scheduler.

NEWPR00001191:     New Object: AIx: Setup input behavior problem.

If set the input Setup with a value out of range the object doesn't work using the attribute value. (This occurs only if the selected sensor type is not supported by the device).

NEWPR00001367:    Trend file uploaded, the Unit of Measure label is not correct for some Object Outputs.

Uploading the Trend file either via FX CommPro N2Open or via WEB site the Unit of Measure label is not correct for the following Data Types :

- SNVT_147, label shown "°C" should be "°C diff";

- SNVT_55, label shown "#" should be "%";

- SNVT_57, label shown "#" should be "W";

- SNVT_59, label shown "#" should be "Pa";

- SNVT_63, label shown "#" should be "°C";

- SNVT_64, label shown "#" should be "s".

NOTE :

the value is always correct.

File Name:		SSM4364 - 03001.a37

Firmware ID:	Fx06 - v3.00.a37

Device: 		FX06 controller

Release date:	Dec 22, 2006

Release reason:	Fixing

Issue document:	No document

Renamed FW with version 3.00  in order to differentiate it from version 2.32 for 32 k EEProm

File Name:		SSM4364_02001_B.a37

Firmware ID:	Fx06 - v2.00 - Eeprom 64KB.a37

Device: 		FX06 controller

Release date:	October 10, 2006

Release reason:	Enhancement

NOTE: Firmware never released

Added features:

Application Management

- Trend management

- Upgraded object library (see below)

Local display

- Time scheduler management

- Event History management

Remote display management

- Event History management

- Trend management

Events

- Storage (Event History)

Supervisor link

- Trended data file upload

Following new objects have been added to the device’s object library:

Extended objects

Extended Analogue Input

Extended Digital Input

Extended Occupancy Input

Extended Span

Extended Analogue output

Extended On Off controller

Extended PAT Object

Extended DAT Object

Extended Damper object

Multi Input Objects

8 Input Maximum

8 input Average

8 input Selector

4 input Not

8 input And

8 input Or

8 input Xor

Extension Modules

NRM Sensor driver

File Name:		SSM4364_01300_B.a37

Firmware ID:	Fx06 - Rel1a - v1.03.a37

Device: 		FX06 controller

Release date:	May 31, 2006

Release reason:	Fixing

The following defects have been fixed:

NEWPR00001109:	FX06/14 LON Cross Reference Table management

“If the LON Cross Reference Table is greater than 128 bytes, is truncated when uploaded to the LON board”

File Name:		SSM4364_01200_B.a37

Firmware ID:	Fx06 - Rel1a - v1.02.a37

Device: 		FX06 controller

Release date:	May 12, 2006

Release reason:	Fixing

The following defects have been fixed:

NEWPR00000607:	FX06/14 User Interface Keypad : swap the "Confirm/Enter" and "Esc/Cancel" buttons.

“For similarity with the existing FX User Interfaces, we require to swap the Confirm/Enter and Esc/Cancel buttons of the user interface of the FX06, FX14 and FX07.”

File Name:		SSM4364_01100_B.a37

Firmware ID:	Fx06 - Rel1a - v1.01.a37

Device: 		FX06 controller

Release date:	March 10, 2006

Release reason:	Release to Beta

The following defects have been fixed:

NEWPR00000661:	FX06P2x doesn't work with the correct Channels set in PAT object.

“The Device works with Channels 3 and 4, instead of Channels 1 and 2 as set in the application”

NEWPR00000634:	FX06 Feedback from Beta Site : potential problem over the N2 Bus

“It happens that randomly the displayed values (either via FX CommPro and the FX06 User Interface) go offline/invalid for a while and then go back to normal. It seems repeatable every 2-3 min”

File Name:		SSM4364_01029_B.a37

Firmware ID:	Fx06 - Rel1a - v1.00 08_02_2006.a37

Device: 		FX06 controller

Release date:	February 8, 2006

Release reason:	Fixing

The following defects have been fixed:

NEWPR00000527:	Convert Object to be added to the supported objects list

“The FX06 could be used for Berg Chilling opportunity, and they require this object." (C. Lane)

File Name:		SSM4364_01028_B.a37

Firmware ID:	Fx06 - Rel1a - v1.00 31_01_2006.a37

Device: 		FX06 controller

Release date:	January 31, 2006

Release reason:	Fixing

The following defects have been fixed:

NEWPR00000518:	Application doesn't work properly after a Power On and Power off cycle.

Power Off the Device. When Power On the Device, all DO’s switch on and they don't work properly

File Name:		SSM4364_01027_B.a37

Firmware ID:	Fx06 - Rel1a - v1.00 16_12_2005.a37

Device: 		FX06 controller

Release date:	Dicember 16, 2005

Release reason:	Fixing

The following defects have been fixed:

NEWPR00000315:	AppKey doesn't work properly

It is not possible download and upload applications with AppKey

NEWPR00000391:	PWM output doesn't work

The PWM output of the controller doesn't work. The duty cycle in output does not reflect the commanded value

File Name:		SSM4364_01015_B.a37

Firmware ID:	Fx06 - Beta v1.15.a37

Device: 		FX06 controller

Release date:	September 30, 2005

Release reason:	First issue

Features list

Application Management

- Stand-alone execution

- Distributed application execution as slave

Remote display management

- Detection

- Application Check

- Application download

- Timestamp synchronization

- Edit variables

- Time scheduler management

- Alarm management

- LEDs management

- Enabler management

- Password management

Local display

- Detection

- Application check

- Menu navigation

- Display parameters

- Modify parameters

- Event notification

- Edit Modem/SMS configuration

- Icons management

- Enabler management

- Password management

Events

- Detection

GSM Modem management

- Detection

- Monitoring field signal

- Send event

- ACK event

- List activ events

- N2Open over RS-232

Supervisor link

- Identify device

- Explore profile

- Read parameter

- Write parameter

- Unit of measurement

- Download

- Application

- Firmware

Programming key

- Detection

- Cohesistence with a remote display

- Download

- Application

- Upload Application

Known defects:

NEWPR00000366:	The application download with the AppKey on the FX06/14 is not always correct.

- Download by FXCommproN2 an application on device FX06/14;

- Upload the application by the device on the AppKey;

- Modify a parameter by display;

- Download the application (previous uploaded) by AppKey on device;

- The download is not correct, Local display shows "CHECKSUM ERROR";

NEWPR00000062:	Fault Test GSM is not correctly managed.

- Power-On the modem GSM (digicom) ;

- Power-On the device ;

- Generate an Event notified on Sms ;

- Device generates Event "Comm Fail" (correct) ;

- Power-On the modem GSM ;

- Generate an Event notified on Sms ;

- Event is not notified on Sms ;

NEWPR00000077:	FX Key doesn't always work properly (erase operation)

- Connect the FX Key on FX06 Display

- Press the button for 15 second to erase the memory

- After 3 seconds on FX06 starts the application download

- The Device remains in Downloading Mode and on the FX Key the two leds blink quickly

NEWPR00000181:	No feedback of the FX key operation on the local display

When Key is plugged-In the FX06 Display doesn't show any diagnostic messages

NEWPR00000253:	System event sending is not managed.

System event are not sent.

NEWPR00000404:	Time and Date problem after power down/up

1) Donwload the application "FX14_LON Test_SendHB_RcvHB.apd" and with the MUI connected to the device verify that the time and date are correct.

2) Turn Off / On the device. The time and date are correct.

3) Donwload the application "FX14_ LON_ LargeForAppKey.apd" and with the MUI connected to the device verify that the time and date are correct.

4) Turn Off / On the device

Result: The time and date are set to 1/1/2048, 00:00:00.

NEWPR00000430:	LON: Stress Test: Network communication error

1) By LonMaker tool commission the FX14 in the attached network (LonMaker Backup file);

2) Try to modify some nvi in the Browser Lon;

Result: sometime a "Network error" message appears in the warning message;

3) Enable the polling in the Browser Lon

Result: A "Communication failure while monitoring the object" message appears very frequently in the warning message;

NEWPR00000428:	LON: Alias Connections behavior

If connect an nvo of the FX14/06  to a two nvi of the another device, only the primary connection works good and the value is correctly trasmitted. The Alias connection doesn't work.

NEWPR00000314:	RTC Object: Attribute BEATOUT is not correctly managed.

If set the Attribute  BEATOUT = 3 , the Output Beatout goes to Low state every second change, instead it should go to Low state every day change.

NEWPR00000109:	FX06 Events: Variable nciEnumeration (10175) is not managed correctly.

- Build an application with to profile a variable nciEnumeration (10175)

- Add variable to device

- Associate an event to ALL variable states

- When save the application, the FxBuilder shows the following Error Report:

Overflow di un'operazione aritmetica.

NEWPR00000107:	FX06: Alarm visualization on MUI is not correct.

Define on Event Maker an alarm with EventName greater than 20 characters.

The Alarm visualization in Event Summary on MUI is not correct.

NEWPR00000125:	FXCommProN2: Download Fail is not correctly managed.

- Download an Application

- During the download, remove the communication between device and CommProN2;

- The progress Bar goes on, but it should stop

- The Error shown " Server Error N.8" should contain more information