File Name:		SSM4378_3.23.0_B.a37

Firmware ID:	Fx07 - v3.23.00.a37

Device: 		FX07 controller

Release date:	March 16, 2009

Release reason:	Fixing

Issue document:	LO1661-09

Following defects have been fixed:

| PT140227 | MASTER SLAVE COMMUNICATION | Time scheduler output status sent from master to slave is sometimes lost on the slave |
| --- | --- | --- |

File Name:		SSM4378_3.21.0_B.a37

Firmware ID:	Fx07 - v3.21.00.a37

Device: 		FX07 controller

Release date:	September 15, 2008

Release reason:	Fixing

Issue document:	LO1627-08

Following issues have been fixed

| PROBTRAK | CQ | DESCRIPTION |
| --- | --- | --- |
| 138206 | 2976 | Display unit of measure with remote display |
| 140051 | 2975 | NRM communication. Some FX messages have an incomplete checksum. It makes unreliable some values on NRM display (i.e.: situation occurs with application where temperatureoffset parameter was set from tool at a value different from 0) |

Feedback from field shows that FX07 (230V model) was affected by strong electromagnetic disturbances (higher than the CE homologations). As a Consequence AD converter of the analogue inputs blocked and sensor measurements were frozen. In order to improve device robustness, AD converter firmware management has been modified (periodic reset in order to prevent any AI freeze situation)

File Name:		SSM4378_3.20.3_B.a37

Firmware ID:	Fx07 - v3.20.03.a37

Device: 		FX07 controller

Release date:	June 6, 2008

Release reason:	Fixing

Issue document:	LO1607-08

Following issues have been fixed

| PROBTRAK | CQ | DESCRIPTION |
| --- | --- | --- |
| 139329 | 2785 | MODEM: ODD phone number not supported |
| 138727 | 2860 | N2 COMMUNICATION: Override and release N2 command not well supported |
|  | 2654 | OBJECT: Clock and date set object revision, Daylight saving bug when clock was modified within the week before the clock change |
|  | 2814 | OBJECT: PAT object revision, Priority change between normal operations and resynch cycle |
|  | 2856 | OBJECT: shared object list (semi-hermetic compressor, EWMA) |
|  | 2861 | OBJECT: New on-off output object revision, Antisticking and short cycle functions not working |
|  | 2931 | OBJECT: AO behavior at disable, At disable active, output was set to 0%. On the contrary DO output was frozen. AO behavior has been aligned with DO one. AO is now frozen when disable |
| 139865 | 2938 | NRM: unplug issue, NRM was not recovered after communication bus unplugged |

File Name:		SSM4378_3.17.0_B.a37

Firmware ID:	Fx07 - v3.17.a37

Device: 		FX07 controller

Release date:	November 7, 2007

Release reason:	Fixing

Issue document:	LO1563-07

Following issues have been fixed

| CQ Number | Description |
| --- | --- |
| NEWPR00001449 | INTEGRATED DISPLAY: Alarm acknowledgment implementation |
| NEWPR00001460 | INTEGRATED DISPLAY: Sub menu of the On-off scheduler was not always shown |
| NEWPR00001551 | INTEGRATED DISPLAY: “too many exceptions” system string didn’t scroll (only “too” was visible) |
| NEWPR00001974 | MEMORY: allocated backup memory was 62 bytes instead of 64 |
| NEWPR00002296 (PT 137968) | INTEGRATED DISPLAY: when event history was displayed, icons disappear and come back only if even status changes |
| NEWPR00002348 | PWM output: PWM went randomly to 0 |
| NEWPR00002388 | INTEGRATED DISPLAY: event pop up new management, when all current events are no more active, the pop up message disappears too |
| NEWPR00002514 | OBJECT: USD time zones were not properly defined on new clock and date set object |
| NEWPR00002620 | TREND: at circular buffer full, trends are not working properly after device power cycle |
| NEWPR00002646 | Output override feature |
| NEWPR00002666 (PT138976) | The FX06 controller, will sometimes display BYE on the user interface. This may occur after an abrupt power interruption |

File Name:		SSM4378_03200_B.a37

Firmware ID:	Fx07 - v3.02.a37

Device: 		FX07 controller

Release date:	March 09, 2007

Release reason:	Fixing

Issue document:	LO1515-07

The firmware new version  fixes the following defects present on the firmware 3.01

| Clearquest | Title | Details |
| --- | --- | --- |
| NEWPR00001896 (Probtrak 137560) | N2 communication problems: AI/BI regions | Bad answer of the device to a READ or COS command through N2 communication bus 1) Point defines as AI type frequently becomes OffLine 2) COS response is abnormal with point defined as BI type |
| NEWPR00001917 (Probtrak 137620) | N2 communication problems: wrong values sent by device at power on | Field feeback: NVOs(BI) defined as SNVT_switch outputs go ON momentarily when the power supply of FX07 is turned off and on. Solution: device is waiting to be completely initialized before to accept write or read command |

File Name:		SSM4378_03101_B.a37

Firmware ID:	Fx07 - v3.01.a37

Device: 		FX07 controller

Release date:	January 9, 2007

Release reason:	Release to Production

Issue document:	LO1463-06

Features list

Application Management

- Stand-alone execution

- Slave of a distributed application

- Trend management

- Extended object library (see below)

Events

- Detection

- Storage (Event History)

GSM Modem management

- Detection

- Monitoring field signal

- Send event

- ACK event

- List active events

- N2Open over RS-232

Local display

- Detection

- Application check

- Menu navigation

- Display parameters

- Modify parameters

- Event notification

- Edit Modem/SMS configuration

- Icons management

- Enabler management

- Time scheduler management

- Event History management

- Password management

Programming key

- Detection

- Coexistence with a remote display

- Application Download

- Application Upload

Remote display management

- Detection

- Application Check

- Application download

- Timestamp synchronization

- Edit variables

- Time scheduler management

- Alarm management

- LED’s management

- Enabler management

- Password management

- Event History management

- Trend management

Supervisor link

- Identify device

- Explore profile

- Read parameter

- Write parameter

- Unit of measurement

- Application Download

- Firmware Download

- Trended data file upload

The following defects have been fixed:

NEWPR00001863:	Calibration Error.

“Calibrations of the Ratio metric sensor are not retained”.

Following new objects have been added to the device’s object library:

Extended objects

Extended Analogue Input

Extended Digital Input

Extended Occupancy Input

Extended Span

Extended Analogue output

Extended On Off controller

Extended PAT Object

Extended DAT Object

Extended Damper object

Multi Input Objects

8 Input Maximum

8 input Average

8 input Selector

4 input Not

8 input And

8 input Or

8 input Xor

Extension Modules

NRM Sensor driver

Known defects:

NEWPR00000107:	FX06: Alarm visualization on MUI is not correct.

Define on Event Maker an alarm with EventName greater than 20 characters.

The Alarm visualization in Event Summary on MUI is not correct.

NEWPR00000430:	LON: Stress Test: Network communication error

1) By LonMaker tool commission the FX14 in the attached network (LonMaker Backup file);

2) Try to modify some nvi in the Browser Lon;

Result: sometime a "Network error" message appears in the warning message;

3) Enable the polling in the Browser Lon

Result: A "Communication failure while monitoring the object" message appears very frequently in the warning message;

NEWPR00000428:	LON: Alias Connections behavior

If connect an nvo of the FX14/06  to a two nvi of the another device, only the primary connection works good and the value is correctly trasmitted. The Alias connection doesn't work.

NEWPR00001480:	LCD2x4 : the sub-menu for the "OnOff Scheduler" is not always shown.

The "OnOff Schedulers" sub-menu is NOT shown, on the Local Display of the Device, if the order of the Scheduler points in the Display "LCD2x4" is the following :

1) Calendar (40070);

2) OnOff Scheduler (40060);

3) OnOff Scheduler Alternate (40061).

The sub-menu is correctly shown in case of different order

NEWPR00001548:	Sms Management : The Event via SMS is not sent after a GSM Modem power-off/power-on:

Operations to repeat the problem :

- FX06 connected to a GSM Modem

- Power-On the Configuartion (Modem and Device);

- Enable an event with associated SMS notification, the SMS is correctly sent;

- Power-Off GSM Modem;

- Power-On GSM Modem;

- Enable an event with associated SMS notification, the SMS is not sent;

To restore the correct behavior the user has to Power-Off and Power-On the device;

Note : the same problem has been verified disconnecting the cable from Modem to Device.

NEWPR00001551:     The "Too Many Exception" system text doesn't scroll.

This system text appears when more than 25 events are defined for the Calendar Scheduler.

NEWPR00001191:     New Object: AIx: Setup input behavior problem.

If set the input Setup with a value out of range the object doesn't work using the attribute value. (This occurs only if the selected sensor type is not supported by the device).

NEWPR00001367:    Trend file uploaded, the Unit of Measure label is not correct for some Object Outputs.

Uploading the Trend file either via FX CommPro N2Open or via WEB site the Unit of Measure label is not correct for the following Data Types :

- SNVT_147, label shown "°C" should be "°C diff";

- SNVT_55, label shown "#" should be "%";

- SNVT_57, label shown "#" should be "W";

- SNVT_59, label shown "#" should be "Pa";

- SNVT_63, label shown "#" should be "°C";

- SNVT_64, label shown "#" should be "s".

NOTE :

the value is always correct.

File Name:		SSM4378 - 03001.a37

Firmware ID:	Fx07 - v3.00.a37

Device: 		FX07 controller

Release date:	Dec 22, 2006

Release reason:	Enhancement

Issue document:	LO1475-06

Firmware version has been aligned with the FX06.

FX06 FW has been changed in order to differentiate it from the 32KBytes E2prom Version.