File Name:		SSM4424_5.1.7_B.a37

Firmware ID:	Fx14_V_0501_07.a37

Device: 		FX14 controller

Release date:	February 18, 2009

Release reason:	Bug fix

Issue Document:	LO1654-09

Following defects have been fixed:

| CQ# | Defect Headline | Defect Description |
| --- | --- | --- |
| 3180 | Test equipment interface | Download request command did not respond with an ACK when downloading calibration coefficients. |
| 3181 | Test equipment interface | Analog Outputs did not respond to commands to output any voltage (always output 0V) before and after calibration. |
| 3182* | Integrated LCD display not operating | Integrated display goes sometimes blank. The controller is still operating but user cannot interact becuase the display is not usable. |

* CQ 3182 has been experienced on FX06 FW version 3.21 only. The fix has been incorporated anyway on FX07 and FX14 devices.

File Name:		SSM4424_5.0.58_B.a37

Firmware ID:	Fx14_V_0500_58.a37

Device: 		FX14 controller

Release date:	November 4, 2008

Release reason:	Bug fix

Issue Document:	LO1628-08

- Fixed errors in FX Programming Key management (Application download operation)

File Name:		SSM4424_5.0.55_B.a37

Firmware ID:	Fx14_V_0500_55.a37

Device: 		FX14 controller

Release date:	September 19, 2008

Release reason:	enhancement

Issue Document:	LO1628-08

- Added IOM management

- Enhanced NRM management  (through Gateway driver)

- Improved ADC protection

- Enhanced PID object:

  - Immediate execution of PID configured with Period larger than minimum after large setpoint changes. The execution period is initialized.

  - Initialization of the execution period, when the PID operating mode returns to auto after any forcing.

- Added Protocol setting by display and protocol dependent settings

- Added Auto Baud Rate

- Default protocol is BACnet

- Default Device Object is MSTP Address

Furthermore, following defects have been fixed:

| ProbTrack | Defect Headline | Defect Description |
| --- | --- | --- |
| 138206 | UoM management with remote display | Using the remote display UoM not maintained after power off. |
| 139329 | ODD phone number | Modem communication with odd numbers |
| 139865* | NRM Local bus recovering | When NRM is disconnected, normal displaying is not recoverd. |
| 140186* | NRM communication | Some FX messages have a wrong checksum, forcing some values on NRM display to be unreliable. |

* Fixed indirectly, due to the different implementation of the driver

File Name:		SSM4424_4.3.1_B.a37

Firmware ID:	Fx14_Rel3a_0403_01.a37

Device: 		FX14 controller

Release date:	December 18, 2007

Release reason:	Bug fix

Issue Document:	LO1580-07

Following defect have been fixed:

| CQ Number | Description |
| --- | --- |
| NEWPR00002714 | Peer to peer doesn't work |

File Name:		SSM4424_4.2.2_B.a37

Firmware ID:	Fx14_Rel3a_0402_02.a37

Device: 		FX14 controller

Release date:	November 29, 2007

Release reason:	Bug fix

Issue Document:	LO1574-07

Following defect have been fixed:

| CQ Number | Description |
| --- | --- |
| NEWPR00002707 | Firmware version returned to test facility inquiry is wrong |

File Name:		SSM4424_4.2.1_B.a37

Firmware ID:	Fx14_Rel3a_0402_01.a37

Device: 		FX14 controller

Release date:	November 22, 2007

Release reason:	Bug fix

Issue Document:	LO1572-07

Following defect have been fixed:

| CQ Number | Description |
| --- | --- |
| NEWPR00002682 | Adding or Removing a Calendar entry with AddListEment or RemoveListElement services, the device reboots |

File Name:		SSM4424_4.1.34_B.a37

Firmware ID:	Fx14_Rel3a_0401_34.a37

Device: 		FX14 controller

Release date:	October 30, 2007

Release reason:	Bug fix

Issue Document:	LO1565-07

Following defect have been fixed:

| CQ Number | Description |
| --- | --- |
| NEWPR00002652 | Weekly Schedule Object : the WeeklySchedule property writes are not correctly managed |
| NEWPR00002650 | Calendar Object : the write of the Datelist property is not correctly managed |
| NEWPR00002649 | MultiState Value object : the value is not correct for the Object associated to an FX Application Point Output. |
| NEWPR00002644 | Distributed Application is not correctly managed. |
| NEWPR00002641 | Binary Output : The Polarity Property of the Slave Device, is not updated via BACnet on Master |
| NEWPR00002640 | Get Event Information Service : The device answers with a wrong Year to this service. |

File Name:		SSM4424_4.1.31_B.a37

Firmware ID:	Fx14_Rel3a_0401_31.a37

Device: 		FX14 controller

Release date:	October 10, 2007

Release reason:	Pilot run

Features list

Application Management

- Extended object library

- Stand-alone execution

- Trend management

Events

- Detection

- Storage (Event History)

Local display

- Detection

- Application check

- Menu navigation

- Display parameters

- Modify parameters

- Icons management

- Enabler management

- Password management

- Time scheduler management

- Event notification

- Event Ack management

- Event History management

Supervisor link

- BACnet B-AAC

- Schedule management

- Event Enrolment

- COV subscription

- Peer-to-peer

- Download

  - Application

  - Firmware

Remote display management

- Detection

- Application Check

- Application download

- Time stamp synchronization

- Edit variables

- Time scheduler management

- Alarm management

- LEDs management

- Enabler management

- Password management

- Event History management

- Trend management

Programming key

- Detection

- Coexistence with a remote display

- Download

- Application

- Upload Application

Known defects:

NEWPR00002037:	Device Object: the Location property is not always reported correctly

The answer to a read property multiple with a lot of Device Object Properties is sometimes incorrect, reporting an  EMPTY value of the Location property.

All other properties values are correct.

NEWPR00001926:	The configuration download versus Display sometimes fails

The download of a big display applications on the MUI has a 50% of probability to fail

Powering off/on the MUI will recover.

NEWPR00001590:	The MSV BACnet Object associated to EE doesn't work in a specific configuration.

The MSV BACnet Object associated to EE doesn’t work for Event on Application Point Input

NEWPR00002640:	Get Event Information Service : The device answers with a wrong Year to this service.

Sending to the device the GetEventInformation Service, the Device answers always with a wrong year