File Name:		SSM4366_4.4.1-CM.a37

Firmware ID:	SSM_4366_04401-CM.a37

Device: 		FX15 controller

Release date:	July 31, 2007

Release reason:	Fixing

Issue document:	LO1621-08

FX15 firmware has been upgraded to solve field situations where electrical disturbances on the power supply affect the device functioning.  Consequence was an instable acquisition from the microprocessor of the power supply frequency (50/60Hz) and instable internal calculation (AI values,…) . Modification makes the firmware algorithm stable.

Fixing has been made according to field feedback (Japan) but similar situation was tracked previously on probtrak 139357

Verification test have been also made to control device behaviour with NAE/FX40 supervisors (PT138727 -NAE- and 139380 -FX40-). Behaviour is correct.

New firmware implements also the new PAT object version

File Name:		SSM4366_4.3.6-CM.a37

Firmware ID:	SSM_4366_4306-CM.a37

Device: 		FX15 controller

Release date:	October 10, 2007

Release reason:	Fixing

EC REF:                   LO1561-07

Following issues have been fixed

| CQ Number | Description |
| --- | --- |
| NEWPR00001361 | INTEGRATED DISPLAY: backlight timeout has been set to 60 seconds (instead of 30) |
| NEWPR00001781 | LOCAL BUS: communication lost between FX15 and XT |
| NEWPR00001917 (PT137620) | INITIALIZATION: profile parameter went to casual values at FX15 power up. Initialization process has been implemented (NACK answer until FX15 is fully ready) |
| NEWPR00002303 (PT137725) | LOCAL BUS: at XP output override from supervisor, FX15 lost the communication |
| NEWPR00002454 | FIRMWARE DOWNLOAD: modification to implement of the multi-firmware download feature of new Commpro 5 |
| NEWPR00002470 | INTEGRATED DISPLAY: the preference point “Date format” didn’t work on local display |
| NEWPR00002482 (PT 138469) | BACKWARD COMPATIBILY: old application files (app-cfg) are now supported |
| NEWPR00002507 (PT138457) | OBJECT: at override through supervisor/commpro, AO value went and stayed invalid |
| NEWPR00002514 | OBJECT: USD time zones were not properly defined on new clock and date set object |

File Name:		SSM4366_04200_CM.a37

Firmware ID:	SSM_4366_04200-CM.a37

Device: 		FX15 controller

Release date:	March 15, 2006

Release reason:	Fixing

EC REF:                   LO1516-07

The following defects have been fixed:

| Clearquest | Title | Details |
| --- | --- | --- |
| NEWPR00001865 (Probtrak 137348 and 137452) | Local bus communication problem: FX with XT/XP | Communication between FX15 and XT fails regularly: 2 sec regular comm, 25 sec comm fail and so on. Configuration: LP-FX15D11-000C Rev. A L0702 LP-DIS60P10-0C L0644 LP-XT91D00-00C L0651 LP-XT91D02-000C L0648 XP-9104-8304 L0622 It was observed that removing MUI from the local Bus communication does not fail. |

File Name:		SSM4366_04000_CM.a37

Firmware ID:	SSM_4366_04000-CM.a37

Device: 		FX15 controller

Release date:	October 26, 2006

Release reason:	Fixing

EC REF:                   LO1476-06

The following defects have been fixed:

NEWPR00001625	FX15 -   AI incorrect readings  & Compro N2 dwnld problems

Problem raised by C.Lane (Mail Oct 12):

With FW 03.2.09 on FX15 and attached apd two problems occurs:

1) AI readings not correct (shown '?' or INV or blank in Compro N2)

2) Download with Compro n2 of apd not always successful.

32-09?

Same apd used on a device with FW 03.1.03 does not fails