File Name:		SSM4361_4.5.3-CM.a37

Firmware ID:	SSM_4361_04503-CM.a37

Device: 		FX16 controller

Release date:	July 28, 2008

Release reason:	Bug Fixing

Issue document:	LO1619-08

Firmware has been upgraded in order to make compatible FX16D devices with future FX hardware extensions development. Introduction of new extensions to be supported by FX devices modifies the initialization time of these device. If these devices are used as FX16D slave, communication could fail at initialization. New firmware corrects this situation.

Verification test have been also made to control device behaviour with NAE/FX40 supervisors (PT138727-NAE- and PT139380 -FX40-). Behaviour was correct for PT138727. On the contrary behaviour was not correct with PT139380 and has been fixed.

PT139380 Note: when FX devices is power cycle, device is not correctly recovered by FX40

New firmware implements also the new PAT object version.

File Name:		SSM4361_4.4.5-CM.a37

Firmware ID:	SSM_4361_04405-CM.a37

Device: 		FX16 controller

Release date:	November 16, 2007

Release reason:	Bug Fixing

Following issues have been fixed

| CQ Number | Description |
| --- | --- |
| NEWPR00002377 | Local bus communication with FX15 slaves is sometimes lost (similar issue found on MD) |
| NEWPR00002484 (PT138418) | VSD DEVICE: implementation of the possibility to pilot a VSD device (branded cutler Hammer) on the local bus as virtual XT/XP |
| NEWPR00002514 | OBJECT: USD time zones were not properly defined on new clock and date set object |
| NEWPR00002559 | TREND: email trend periodic notification improvement (initial problem coming from FX-Builder data base export) |
| NEWPR00002560 | MUI: event history page visualization fixing |
| NEWPR00002651 | Change of a SNVT105 is not communicated as far as it is less than 0,5°C |

Note: as XT/XP management has been modified to support VSD device, regression tests have been made with following XT/XP configurations

-  XT9100 + XP9103

-  XT9100 + 2x XP9103

-  XT9100 + XP9105

-  XT9100 + 2x XP9105

File Name:		fx16max_V42-00.a37

Firmware ID:	SSM_4361_04200-CM.a37

Device: 		FX16 controller

Release date:	November 16, 2006

Release reason:	Bug Fixing

The following defects have been fixed:

NEWPR00001674		The Trends visualization on MUI doesn't work.

A few minutes after the FX16 power-on, it is no more possible to see the trends on MUI. In fact if the user searches to entry in Trend Page, the MUI shows "waiting" and then it exits automatically from trends folder.

The Periodic Off-Load is sent by email correctly.

Using FX16 with fw fx16max_V41-09.a37, the trends visualization and sending via email are correct.

File Name:		fx16max_V41-11.a37

Firmware ID:	SSM_4361_04111-CM.a37

Device: 		FX16 controller

Release date:	October 10, 2006

Release reason:	Bug Fixing

The following defects have been fixed:

NEWPR00001556		The LED on Remote Display doesn't work after opening of the "OnOff Scheduler" Display page.

In order to repeat the problem, the following steps have to be executed :

- download the attached application "LED Bug.apd" in a FX16 Device, the Remote Display (MUI) is connected to the Device; in the application, the MUI red LED becomes ON if the Digital Input 1 is put to ON (contact closed);

- put to ON the Digital Input 1, the MUI red LED becomes ON, the behaviour is correct;

- put to OFF the Digital Input 1, the MUI red LED becomes OFF, the behaviour is correct;

- now open the "OnOff Scheduler" Display page, if the Digital Input 1 is put to ON the LED doesn't work, remains OFF. This is NOT correct.

- after the opening of the "OnOff Scheduler" Display page, the LED doesn't work. It is necessary to power-down and power-up the Device to restore the LED behaviour.

NOTEs :

1) the problem is verified also on the FX16+;

2) the problem is verified also after enter in the "OnOff Scheduler Alternate" Display page.

NEWPR00001499:	Cannot Consistently Download Application with FX CommPro N2

I cannot consistently download the attached application to an FX16.  My success rate is around 50%.

Details of the problem:

FX Compro N2    1.1.10

FX16 N2 Address 1

FX16 FW  04.1-03

MUI FW 2.43

Additional tests done in Lomagna showed different behaviour changing FX16 device. The occurrence of the failure has not a clear pattern, but the problem is present.

Problem happens both with Zoning apd attached (Builder 4.0.26) and with Zoning apd currently in production (Builder 3.8.1)