File Name:		SSM4425_7.1.6_B.a37

Firmware ID:	SSM4425.7.1.06-CM.a37

Device: 		FX16 controller

Release date:	March 6, 2009

Release reason:	Enhancement

Issue Document:	LO1658-09

Added XM Module management

File Name:		SSM4425_6.3.1_B.a37

Firmware ID:	SSM_4540_06301-CM.a37

Device: 		FX16 controller

Release date:	December 18, 2007

Release reason:	Bug fix

Issue Document:	LO1580-07

Following defect have been fixed:

| CQ Number | Description |
| --- | --- |
| NEWPR00002714 | Peer to peer doesn't work |

File Name:		SSM4425_6.2.1_B.a37

Firmware ID:	SSM_4540_06201-CM.a37

Device: 		FX16 controller

Release date:	November 22, 2007

Release reason:	Bug fix

Issue Document:	LO1572-07

Following defect have been fixed:

| CQ Number | Description |
| --- | --- |
| NEWPR00002682 | Adding or Removing a Calendar entry with AddListEment or RemoveListElement services, the device reboots |

File Name:		SSM4425_6.1.62_B.a37

Firmware ID:	SSM_4540_06162-CM.a37

Device: 		FX16 controller

Release date:	October 30, 2007

Release reason:	Bug Fix

Issue Document:	LO1565-07

Following defect have been fixed:

| CQ Number | Description |
| --- | --- |
| NEWPR00002652 | Weekly Schedule Object : the WeeklySchedule property writes are not correctly managed |
| NEWPR00002650 | Calendar Object : the write of the Datelist property is not correctly managed |
| NEWPR00002649 | MultiState Value object : the value is not correct for the Object associated to an FX Application Point Output. |
| NEWPR00002644 | Distributed Application is not correctly managed. |
| NEWPR00002641 | Binary Output : The Polarity Property of the Slave Device, is not updated via BACnet on Master |
| NEWPR00002640 | Get Event Information Service : The device answers with a wrong Year to this service. |

File Name:		SSM4425_6.1.59_B.a37

Firmware ID:	SSM_4540_06159-CM.a37

Device: 		FX16 controller

Release date:	October 10, 2007

Release reason:	Pilot run

Features list

Application Management

- Extended object library

- Stand-alone execution

- Trend management

Events

- Detection

- Storage (Event History)

Local display

- Detection

- Application check

- Menu navigation

- Display parameters

- Modify parameters

- Icons management

- Enabler management

- Password management

- Time scheduler management

- Event notification

- Event Ack management

- Event History management

Supervisor link

- BACnet B-AAC

- Schedule management

- Event Enrolment

- COV subscription

- Peer-to-peer

- Download

  - Application

  - Firmware

Remote display management

- Detection

- Application Check

- Application download

- Time stamp synchronization

- Edit variables

- Time scheduler management

- Alarm management

- LEDs management

- Enabler management

- Password management

- Event History management

- Trend management

Programming key

- Detection

- Coexistence with a remote display

- Download

- Application

- Upload Application

Known defects:

NEWPR00002037:	Device Object: the Location property is not always reported correctly

The answer to a read property multiple with a lot of Device Object Properties is sometimes incorrect, reporting an  EMPTY value of the Location property.

All other properties values are correct.

NEWPR00001926:	The configuration download versus Display sometimes fails

The download of a big display applications on the MUI has a 50% of probability to fail

Powering off/on the MUI will recover.

NEWPR00001590:	The MSV BACnet Object associated to EE doesn't work in a specific configuration.

The MSV BACnet Object associated to EE doesn’t work for Event on Application Point Input

NEWPR00002640:	Get Event Information Service : The device answers with a wrong Year to this service.

Sending to the device the GetEventInformation Service, the Device answers always with a wrong year