File Name:		SSM4447_1.3.0_B.a37

Firmware ID:	XM14_V_0103_00.a37

Device: 		XM14

Release date:	June 19, 2009

Release reason:	Bug fix

Issue document:	LO1674-09

The following defects have been fixed:

| CQ# | Defect Headline | Defect Description |
| --- | --- | --- |
| 3423 | XM 14 wrong AI update from network | Problem updating from network the object reference up the first three |

File Name:		SSM4447_1.2.1_B.a37

Firmware ID:	XM14_V_0102_01.a37

Device: 		XM14

Release date:	May 29, 2009

Release reason:	Bug fix

Issue document:	LO1670-09

Following defects have been fixed:

| CQ# | Defect Headline | Defect Description |
| --- | --- | --- |
| 3382 | XM07/XM14 beta site issue with the UI set as AI | XM07/XM14beta site issue. UIs configured as AIs with 0-10V do not respond with the 0-10V signal. |

File Name:		SSM4447_1.1.1_B.hex

Firmware ID:	XM14_V_0101_01.a37

Device: 		XM14

Release date:	February 27, 2009

Release reason:	Bug fix

Issue document:	LO1655-09

Following defects have been fixed:

| CQ# | Defect Headline | Defect Description |
| --- | --- | --- |
| 3180 | Test equipment interface | Download request command did not respond with an ACK when downloading calibration coefficients. |
| 3181 | Test equipment interface | Analog Outputs did not respond to commands to output any voltage (always output 0V) before and after calibration. |
| 3184 | Object Output override/release issue | if the output of an object is overridden from the network and then locally (via manual override switches or pots) when the manual override is released, value written from the network is lost. This occurs in BACnet when writing at priority 16 and always in N2Open |

File Name:		SSM4447_1.0.39_B.hex

Firmware ID:	XM14_V_0100_39.a37

Device: 		XM14

Release date:	September 23rd, 2008

Release reason:	RTP

Issue document:	--

- Corrected bug (DI11 & DI12 Configuration was coupled)

- Added protection against ADC freezing of AI values

File Name:		SSM4447_1.0.37_B.hex

Firmware ID:	XM14_V_0100_37.a37

Device: 		XM14

Release date:	July 30th, 2008

Release reason:	RTP

Issue document:	--

Following defects have been fixed:

- UI5 and UI6 not correctly commanded as DI (inverted).

File Name:		SSM4447_1.0.34_B.hex

Firmware ID:	XM14_V_0100_34.a37

Device: 		XM14

Release date:	June 25th, 2008

Release reason:	RTP

Issue document:	--

File Name:		SSM4447_1.0.20_B.hex

Firmware ID:	XM14_V_0100_20.a37

Device: 		XM14

Release date:	April 29th, 2008

Release reason:	RTM

Issue document:	RTM6394