File Name:		SSM4445_3.3.5_B.a37

Firmware ID:	SSM4445_3.3.5_B.a37

Device: 		MD20 controller

Release date:	September 12, 2008

Release reason:	Bug fixing

Issue document: 	LO1622-08

Firmware has been upgraded in order to make compatible MD devices with future FX hardware extensions development. Introduction of new extensions to be supported by FX devices modifies the initialization time of these devices. If these devices are used as MD slave, communication could fail at initialization. New firmware corrects this situation.

Verification test have been also made to control device behaviour with NAE/FX40 supervisors (PT138727-NAE- and PT139380 -FX40-). Behaviour was correct for PT138727. On the contrary behaviour was not correct with PT139380 and has been fixed.

PT139380 Note: when FX devices is power cycle, device is not correctly recovered by FX40

Complete fixing are listed in the following table

| PROBTRAK | CQ | DESCRIPTION |
| --- | --- | --- |
| - | 943 | The FX Devices doesn't manage in the same mode the Override and Release functions for fields of structured variable |
| - | 2744/2926 | New Slave management (5.xx): restart status and init status |
| 139380 | 2854 (2860) | FX16 behavior after FX40 resets |
| 140067 | 2990 | ODD number (SMS) |
|  | 3006 | Error code 3 after application download (N2 only) NOT APPLICABLE FOR SSM4401 (LON MODEL) |

NOTE FOR ENGINEERING:

Both models, N2 and LON, share the same code and so have the same firmware revision level. However CQ3006 introduces discrepancy between N2 and LON models. This discrepancy has been solved by conditioning the compilation of the code (N2 compiled code and LON compiled code). This disposition has to be maintained by developers for future devices upgrade.

File Name:		SSM4445_3.2.5_B.a37

Firmware ID:	md20_V32-05.a37

Device: 		MD20 controller

Release date:	December 12, 2007

Release reason:	Bug fixing

Issue document: 	LO1578-07

Bug fixing:

Bug fixing common to SSM4401 and SSM4445

| CQ Number | Description |
| --- | --- |
| NEWPR00000266 | GSM modem signals level was wrongly displayed |
| NEWPR00001536/1603 (PT136892) | Alarm acknowledgment via sms was not correctly implemented |
| NEWPR00001782/2299 (PT137323) | Fax notification: text overwritten by fax header text |
| NEWPR00002377 | Local bus communication problem with slaves |

File Name:		md20_V31-02.a37

Firmware ID:	SSM4445_3.1.2-CM.a37

Device: 		MD20 controller

Release date:	October 11, 2007

Release reason:	Released to PDM

Issue document:	EC1562-07

File Name:		md20_V31-02.a37

Firmware ID:	SSM4445_3.1.2-CM.a37

Device: 		MD20 controller

Release date:	November 7, 2006

Release reason:	Bug Fixing

Issue document:	EC1341-05

The following defects have been fixed:

NEWPR0000331		The application download versus MD20D01 (FamilyID = 0601) doesn't work properly

- Device status is "Applicationless", the download operation is correctly executed but the status remains in "Initializing";

- if a power-cycle is executed for the Device, the status is "Stopping"; now if the application is downloaded the operation doesn't start, but a few time the Device goes in "Running" status for the previous downloaded applciation and the FX CommPro shows the message "The Device is not ready";

after that if another application is downloaded the FX CommPro shows the error "Error in setting the Buffer Size : 128".