File Name:		SSM4401_3.3.5_B.a37

Firmware ID:	SSM4401_3.3.5_B.a37

Device: 		MD20 LON controller

Release date:	September 12, 2008

Release reason:	Bug fixing

Issue document: 	LO1622-08

Firmware has been upgraded in order to make compatible MD devices with future FX hardware extensions development. Introduction of new extensions to be supported by FX devices modifies the initialization time of these devices. If these devices are used as MD slave, communication could fail at initialization. New firmware corrects this situation.

Verification test have been also made to control device behaviour with NAE/FX40 supervisors (PT138727-NAE- and PT139380 -FX40-). Behaviour was correct for PT138727. On the contrary behaviour was not correct with PT139380 and has been fixed.

PT139380 Note: when FX devices is power cycle, device is not correctly recovered by FX40

Complete fixing are listed in the following table

| PROBTRAK | CQ | DESCRIPTION |
| --- | --- | --- |
| - | 943 | The FX Devices doesn't manage in the same mode the Override and Release functions for fields of structured variable |
| - | 2744/2926 | New Slave management (5.xx): restart status and init status |
| 139380 | 2854 (2860) | FX16 behavior after FX40 resets |
| 140067 | 2990 | ODD number (SMS) |
|  | 3006 | Error code 3 after application download (N2 only) NOT APPLICABLE FOR SSM4401 (LON MODEL) |

NOTE FOR ENGINEERING:

Both models, N2 and LON, share the same code and so have the same firmware revision level. However CQ3006 introduces discrepancy between N2 and LON models. This discrepancy has been solved by conditioning the compilation of the code (N2 compiled code and LON compiled code). This disposition has to be maintained by developers for future devices upgrade.

File Name:		SSM4401_3.2.5_B.a37

Firmware ID:	md20lon_V32-05.a37

Device: 		MD20 LON controller

Release date:	December 12, 2007

Release reason:	Bug fixing

Issue document: 	LO1578-07

Bug fixing:

Bug fixing common to SSM4401 and SSM4445

| CQ Number | Description |
| --- | --- |
| NEWPR00000266 | GSM modem signals level was wrongly displayed |
| NEWPR00001536/1603 (PT136892) | Alarm acknowledgment via sms was not correctly implemented |
| NEWPR00001782/2299 (PT137323) | Fax notification: text overwritten by fax header text |
| NEWPR00002377 | Local bus communication problem with slaves |

Bug fixing only on SSM4401

| CQ Number | Description |
| --- | --- |
| NEWPR0000170 | Problem with the program ID when the device is applicationless. ProgramID was not upgraded after firmware upgrade and so MD LOADER profile data base and device profile was no more synchronized until MD LOADER was closed and opened again |
| NEWPR00002177 (PT138051/138116) | Download: MD LON remains blocked at 85% (initialization not fully completed) |

File Name:		md20lon_V31-09.a37

Firmware ID:	SSM4401_3.1.9-CM.a37

Device: 		MD20 LON controller

Release date:	October 11, 2007

Release reason:	Released to PDM

Issue document: 	LO1562-07

File Name:		md20lon_V31-09.a37

Firmware ID:	SSM_4401_03109-CM.a37

Device: 		MD20 LON controller

Release date:	December 6, 2006

Release reason:	Bug Fixing

The following defects have been fixed on EC1490-06 (and after production block n°168):

NEWPR00001403		Probtrak 136535 : MDLON: Problems in communication with XT Modules

A problem has been reported from field (ProbTrak will be opened) regarding an application featuring the MD20LON v31_08. Having the following application structure:

MD20LON

-> N2Add(4) Fx15 Classic as Slave

-> N2Add(5) XT+XP9105+XP9103

-> N2Add(6) XT+XP9103+XP9103

Randomly (In terms of time, but always happens) the MDLON looses communication with XT (Add:5) and the LED on the XT Module Start Blinking.

In order to get back communication between the two, a system power cycle is needed. The communication then randomly is lost again.

NEWPR00001624	MDLON: The editing from Lon commissioning tool of the CPs schedulers is not apply by the device

1) Download by MD20 Lon Loader the "MD20D05(V000)_90001106000404E7_(4.0.31) Schedulers.apd" application

2) Commission the device by LonMaker tool using the Resource files generated by Fx-Builder 4.0.31

Results: Open the Lon browser and try to modify for exemple the cpOnOffEvent. The new value is apply by the Lon browser but if verify on the Master display the new value is not write.

NOTE: if modify the cpschedulers using the display of the device all work good.

NEWPR00001633		MDLON: The device restarts after explore by MD20-CommPro Lon

Test condition:

1) Download on one MDLon the application "MD20D03(V000)_9000110600404FC_(3.11.3) SRHB & CoV.apd";

2) Download on another MDLon the application "MD20D04(V000)_9000110600404FD_(4.0.31) SRHB & CoV_(converted)+N2 PlugIn.apd";

3) Commission the devices by LonMaker using the attached network;

4) Decommission the devices;

5) Connect the MD20-CommPro Lon and explore the devices;

Resutls: When the plug-In is loaded after about 15 seconds the device restarts.

NEWPR00001636	MDLON: Error code 37 if download an application with application points not on the network in the Lon plugIn

Download an application that have application points not on the network in the Lon plugIn.

The MDLON shows the error code : 37

NEWPR00001651		MDLON Loader: Download problem at 20% using the MD20D04 (RS232)

(see also NEWPR00001536)

Test condition: MD20D04 (RS232)

1) The device is applicationless

2) Download the application "MD20D04 (RS232)_Clear_No Web_(4.0.34).apd"

Result: download OK

3) Download the application "MD20D04 (RS232)_ 258 NVs_No Web_(4.0.34).apd"

Result: the download failed at 20% (SCPT2 file step).The message appears:"failed to download fileID=2. Retry or Cancell?" In this moment the device is downloading,  If click Retry the tool shows "download failed"  and the device remain in downloading. After a power cycle the device is applicationless.

4) Close the tool MDLon Loader and reopen it. Add the device in the network view and explore it.

Result: The correct MDLon plugIn is shown.

5) Download again the application "MD20D04 (RS232)_ 258 NVs_No Web_(4.0.34).apd"

Result: download OK

Note1: the same problem occurs if there is a modem connected to the RS232

Note2: the problem doesn't appear if use a null modem cable+adapter connected to the RS232