- Install VFD Lon Option Card.   Refer to Vacon LonWorks Option Board User’s Manual included with 32003448-001

- Install FCLoad onto PC.  Open WinZip-fcload[1], then double click on the setup.exe file.  Follow setup instructions on the PC.

- Remove keypad.  Connect VFD to PC via RS232 cable.

- Find and open FCLoad from the PC.

- Click on Application.

- Click on Browse to find Multi-purpose II application (smf089HM.hex)

- Click on Start.  Follow directions at bottom of FCLoad screen.

- Program the Variable Frequency Drive using the Vacon Multi-purpose Control Application II User’s manual.

- Connect correct wiring to I/O terminals.  Use Multi-purpose Application II (page 2) and LonWorks Option Board User’s Manual (page 10)